E.O. VR-201/202 or VR-203/204

Healy Clean Air Separator Static Pressure Performance Test Report Form

| Permit Number: | Test Company: |
| --- | --- |
| Site Name: | Technician: |
| Site Address: | Certification Number | Expiration Date |
| City: | Zip: | District: |  |
| Date/Time of Test: | Franklin (Healy): |  |

| TEST INFORMATION |
| --- |
| Calibration date for digital manometer (must be within 180 days of the test) |  |
| Ending value for digital manometer drift test (must be 0.01 in. w.c. or less) |  |

| VACUUM TEST |
| --- |
| Vacuum at start of test, inches of water column (in. w.c.) |  |
| Vacuum at one minute, in. w.c. |  |
| Vacuum at two minutes, in. w.c. |  |
| Vacuum at three minutes, in. w.c. |  |
| Vacuum at four minutes, in. w.c. |  |
| Final vacuum at five minute, in. w.c. |  |
| Allowable minimum vacuum, in. w.c. (from shaded area below) |  |
| Allowable 5-Minute Vacuum Decay for Clean Air Separator |
| Vacuum at start of test, in. w.c. | 8.0 | 7.0 | 6.0 | 5.0 | 4.0 | 3.0 | 2.0 |
| Minimum vacuum after five min., in. w.c. | 5.5 | 4.7 | 3.8 | 3.0 | 2.2 | 1.5 | 0.8 |

| POSITIVE PRESSURE TEST |
| --- |
| Nitrogen introduction flow rate (must be between 2 and 4 CFM) |  |
| Pressure at start of test, in. w.c. |  |
| Pressure at one minute, in. w.c. |  |
| Pressure at two minutes, in. w.c. |  |
| Pressure at three minutes, in. w.c. |  |
| Pressure at four minutes, in. w.c. |  |
| Final pressure at five minute, in. w.c. |  |
| Allowable minimum pressure, in. w.c. | 1.77 |

I declare, under penalty of perjury under the laws of the state of California that based on information and belief formed after reasonable inquiry, the statements and information provided in this document are true, accurate, and complete.

Signature of Technician:  ________________________________	Date:  ____________________