E.O. VR-203/204

Veeder-Root Vapor Polisher Operability Test Form

| Permit Number: | Test Company: |
| --- | --- |
| Site Name: | Technician: |
| Site Address: | Certification Number | Expiration Date |
| City: | Zip: | District: |  |
| Date/Time of Test: | VST: |  |
|  | Veeder-Root: |  |

| TEST INFORMATION |
| --- |
| Calibration date for digital manometer (must be within 6 months of the test) |  |
| Ending value for digital manometer drift test (must be 0.01 in. w.c. or less) |  |
| Calibration date for thermometer (must be with 6 months of the test) |  |
| Vapor polisher valve close date and time (must have been closed for at least 2 hours) |  |  |
| Atmospheric pressure sensor serial number |  |

| PRESSURE INTEGRITY TEST |
| --- |
| Nitrogen gas flow rate (scfh) |  |
| Starting pressure (in. w.c.) |  |
| Final pressure at 1 minute (in. w.c.) |  |
| Is the final pressure > 7.0 in. w.c.? |  |
| Is the difference between the starting and final pressure < 0.5 in. w.c.? |  |

NOTES:	1If the final pressure is not > 7.0 in. w.c. and the difference is not < 0.5 in. w.c., then the vapor polisher is not in compliance.

| FLOW TEST |
| --- |
| Nitrogen gas flow rate (scfh) |  |
| Pressure (in. w.c.) |  |
| Is the pressure between 1.69 and 2.25 in. w.c.? |  |

NOTES:	1The flow rate must be 18.0 ± 0.2 scfh.

2The pressure must be between 1.69 and 2.25 in. w.c. or the vapor polisher is not in compliance.

3Three-way valve must be returned to normal (open) operating position after testing is completed.

4PMC valve mode must be re-set to automatic after testing is completed.

I declare, under penalty of perjury under the laws of the state of California that based on information and belief formed after reasonable inquiry, the statements and information provided in this document are true, accurate, and complete.

Signature of Technician:  ________________________________	Date:  ____________________

| VAPOR VALVE THERMOMETER TEST |
| --- |
|  | §7.3.2 |
| Vapor polisher ambient temperature |  |
| Vapor polisher outlet temperature |  |
| Difference between ambient and outlet temperatures |  |
| Is the difference less than 10o F? If not, proceed to section 9.2.1 |  |
|  | §9.2.2 |
| Vapor polisher ambient temperature |  |
| Vapor polisher outlet temperature |  |
| Difference between ambient and outlet temperatures |  |
| Is the difference less than 10o F? If not, proceed to section 9.2.4 |  |
|  | §9.2.4 & §9.2.5 |
| Vapor polisher ambient temperature |  |
| Vapor polisher outlet temperature |  |
| Calibrated thermometer ambient temperatures |  |
| Difference between outlet temperature and the calibrated thermometer |  |
| Is the difference less than 10o F? If not, the outlet thermometer does not meet specifications |  |
| Difference between ambient temperature and the calibrated thermometer |  |
| Is the difference less than 10o F? If not, the ambient thermometer does not meet specifications |  |

| UST THERMOMETER TEST |
| --- |
| UST #1 | §7.3.3 |
| T5 temperature |  |
| T4 temperature |  |
| Difference between T5 and T4 temperatures |  |
| Is the difference less than 10o F? If not, proceed to section 9.1 |  |
|  | §9.1 |
| T5 temperature |  |
| Calibrated thermometer ambient temperature |  |
| Difference between T5 and calibrated thermometer |  |
| Is the difference less than 10o F? If not, the T5 thermometer does not meet specifications |  |
| UST #2 | §7.3.3 |
| T5 temperature |  |
| T4 temperature |  |
| Difference between T5 and T4 temperatures |  |
| Is the difference less than 10o F? If not, proceed to section 9.1 |  |
|  | §9.1 |
| T5 temperature |  |
| Calibrated thermometer ambient temperature |  |
| Difference between T5 and calibrated thermometer |  |
| Is the difference less than 10o F? If not, the T5 thermometer does not meet specifications |  |

I declare, under penalty of perjury under the laws of the state of California that based on information and belief formed after reasonable inquiry, the statements and information provided in this document are true, accurate, and complete.

Signature of Technician:  ________________________________	Date:  ___________________

| UST THERMOMETER TEST (cont.) |
| --- |
| UST #3 | §7.3.3 |
| T5 temperature |  |
| T4 temperature |  |
| Difference between T5 and T4 temperatures |  |
| Is the difference less than 10o F? If not, proceed to section 9.1 |  |
|  | §9.1 |
| T5 temperature |  |
| Calibrated thermometer ambient temperature |  |
| Difference between T5 and calibrated thermometer |  |
| Is the difference less than 10o F? If not, the T5 thermometer does not meet specifications |  |
| UST #4 | §7.3.3 |
| T5 temperature |  |
| T4 temperature |  |
| Difference between T5 and T4 temperatures |  |
| Is the difference less than 10o F? If not, proceed to section 9.1 |  |
|  | §9.1 |
| T5 temperature |  |
| Calibrated thermometer ambient temperature |  |
| Difference between T5 and calibrated thermometer |  |
| Is the difference less than 10o F? If not, the T5 thermometer does not meet specifications |  |

| ATMOSPHERIC PRESSURE SENSOR TEST |
| --- |
| Atmospheric pressure sensor reading (psi) |  |
| Atmospheric pressure sensor reading (in. mercury) |  |
| Atmospheric pressure from local source (in. mercury) |  |
| Difference between local source and pressure sensor reading (A) |  |
| 0.10 x local source (B) |  |
| Is A < B? If not, the vapor polisher is not is compliance |  |

NOTES:	1Conversion from pressure (psi) to pressure (in. mercury) is: (psi +14.7) x 2.036

I declare, under penalty of perjury under the laws of the state of California that based on information and belief formed after reasonable inquiry, the statements and information provided in this document are true, accurate, and complete.

Signature of Technician:  ________________________________	Date:  ____________________